## Version Records
Reversion Record
Date | Version | Description | Editor | Auditor
2024-07-04 | V1 | Initial Version | Mikey
2024-07-19 | V2 | DIDO data information supplement | Mikey
2024-07-22 | V3 | Add information on PV and liquid cooling | Mikey
2024-11-28 | V4 | Update write function code and empty point position annotation | Mikey
2025-04-07 | V5 | PCS information update and unit error update | Mikey
2025-05-28 | V6 | PCS information update and Rack and Cell Information update | Mikey
2025-08-18 | V7 | Update write function code(Function Code: 0x16) | Mikey

## Rule description
ModbusTCP communication method description ：
1、In TCP communication, the default EMS is the client and the Mars LC is the server;
2、The default IP address of LC is X.X.X.X and port number 502;
3、Floating point character types are “AB CD” ；
Communication topology reference diagram：

## LC Information
LC Information -- Overview
Register Settings (Modbus Addr:247 Function Code:0x04 - Read Input Registers)
Modbus Addr (ID) : 247
Addr | Equipment | Name | Unit | Type | Notes
0 | LC | Measurement point version number |  | u16
1 | LC | PCS Number |  | u16 | Maximum 50
2 | LC | Bank Number |  | u16 | Maximum 50
3 | LC | Rack Number |  | u16 | Total number of Rack under all banks, maximum 240
4 | LC | Meter Number |  | u16 | Maximum 100
LC Information -- EMS Write into LC
Register Settings (Modbus Addr:247 Function Code: 0x16)
Modbus Addr (ID) : 247
Remote adjustment/Remote control process: 1. Set the energy storage working mode and parameters; 2. Set the end time of remote control; 3. Set EMS working mode to remote control mode; 4. End control: Set EMS working mode to autonomous control mode or wait for remote control timeout to end;
Addr | Equipment | Name | Unit | Type | Description | Notes
0 | LC | EMS Working Mode | - | u16 | 0: Autonomous control mode, does not accept remote control; 1: Remote control mode, accepts remote control
1 | LC | Remote Control Duration | min | i32 | If the value is N, it indicates the control will stop at the Nth whole minute after the current time (excluding the current time) | For example: If the current time is 2023-06-01 10:12:35, and the end time is set to 1, the control will end at 2023-06-01 10:13:00
3 | LC | Energy Storage Working Mode | - | u16 | 0: Grid-connected constant power mode; 1: Off-grid constant voltage mode; 2: Energy storage stop mode
4 | LC | Energy Storage Active Power | W | i32 | In grid-connected constant power mode, the active power on the AC side: <0: Discharging power =0: Idle >0: Charging power
6 | LC | Energy Storage Reactive Power | Var | i32 | Reactive power value | Currently not supporting reactive power control Empty point position annotation
8 | LC | AC Voltage | V | u16 | Output voltage in off-grid constant voltage mode
9 | LC | AC Frequency | 0.01Hz | u16 | Output frequency in off-grid constant voltage mode
LC Information -- EMS Read from LC
Register Settings (Modbus Addr:1 Function Code:0x02 - Read Discrete Inputs)
Modbus Addr (ID) : 1
Addr | Equipment | Name | Unit | Type | Notes
0 | LC | LC Alarm Summary |  | bit | 0: normal ； 1: Alarm
1 | LC | PCS Alarm Summary |  | bit | 0: normal ； 1: Alarm
2 | LC | Bank Alarm Summary |  | bit | 0: normal ； 1: Alarm
3 | LC | Air Conditioning Alarm Summary |  | bit | 0: normal ； 1: Alarm

## PCS Information
LC Information -- EMS Read from LC
Register Settings (Modbus Addr:1 Function Code:0x04 - Read Input Registers)
Modbus Addr (ID) : 1
Notes： 1、All values do not require scaling or adding offset. For example: Measurement point address 16, measurement value 123.4 represents Total AC Active Power of 123.4 kW. 2、Ensure that each read operation is limited to data from at most one device.
Addr | Equipment | Name | Accuracy | Unit | Type | Notes
0 | 1#PCS | Operating Status |  |  | u16 | 0：Stopped，1：Running
1 | 1#PCS | Reserve |  |  | u16
2 | 1#PCS | AC Uab Line Voltage |  | V | float
4 | 1#PCS | AC Ubc Line Voltage |  | V | float
6 | 1#PCS | AC Uca Line Voltage |  | V | float
8 | 1#PCS | AC Phase A Current |  | A | float
10 | 1#PCS | AC Phase B Current |  | A | float
12 | 1#PCS | AC Phase C Current |  | A | float
14 | 1#PCS | AC Frequency |  | Hz | float
16 | 1#PCS | Total AC Active Power |  | kW | float | “+”：charge，“-”：discharge
18 | 1#PCS | Total AC Reactive Power |  | kvar | float
20 | 1#PCS | Total AC Apparent Power |  | kW | float
22 | 1#PCS | Total AC Power Factor |  |  | float
24 | 1#PCS | Phase A AC Active Power |  | kW | float | Empty point position annotation V6 Update Content
26 | 1#PCS | Phase B AC Active Power |  | kW | float | V6 Update Content
28 | 1#PCS | Phase C AC Active Power |  | kW | float | V6 Update Content
30 | 1#PCS | Phase A AC Reactive Power |  | kvar | float
32 | 1#PCS | Phase B AC Reactive Power |  | kvar | float
34 | 1#PCS | Phase C AC Reactive Power |  | kvar | float
36 | 1#PCS | Phase A AC Apparent Power |  | kVA | float
38 | 1#PCS | Phase B AC Apparent Power |  | kVA | float
40 | 1#PCS | Phase C AC Apparent Power |  | kVA | float
42 | 1#PCS | Phase A AC Power Factor |  |  | float
44 | 1#PCS | Phase B AC Power Factor |  |  | float
46 | 1#PCS | Phase C AC Power Factor |  |  | float
48 | 1#PCS | IGBT Module Temperature |  | ℃ | float
50 | 1#PCS | Ambient Temperature |  | ℃ | float
52 | 1#PCS | Total AC Charging Energy |  | kWh | float
54 | 1#PCS | Total AC Discharging Energy |  | kWh | float
56 | 1#PCS | Daily AC Charging Energy |  | kWh | float
58 | 1#PCS | Daily AC Discharging Energy |  | kWh | float
60 | 1#PCS | Number of branches |  | 1 | u32
62 | 1#PCS | Branch 1 DC Power |  | kW | float
64 | 1#PCS | Branch 1 DC Voltage |  | V | float
66 | 1#PCS | Branch 1 DC Current |  | A | float
68 | 1#PCS | Branch 2~n DC Power |  | kW | float | Empty point position annotation
70 | 1#PCS | Branch 2~n DC Voltage |  | V | float
71 | 1#PCS | Branch 2~n DC Current |  | A | float
...
100 | 2#PCS | Operating Status |  |  | u16 | 0：Stopped，1：Running
101 | 2#PCS | Reserve |  |  | u16
102 | 2#PCS | AC Phase A Voltage |  | V | float
...
4900 | 50#PCS | Operating Status |  |  | u16 | 0：Stopped，1：Running
4901 | 50#PCS | Reserve |  |  | u16
4902 | 50#PCS | AC Phase A Voltage |  | V | float

## Bank Information
LC Information -- EMS Read from LC
Register Settings (Modbus Addr:1 Function Code:0x04 - Read Input Registers)
Modbus Addr (ID) : 1
Notes： 1、All values do not require scaling or adding offset. For example: Measurement point address 5000, measurement value 456.7 represents bank voltage of 456.7V. 2、Ensure that each read operation is limited to data from at most one battery bank .
Addr | Equipment | Name | Accuracy | Unit | Type | Notes
5000 | 1#battery bank | Bank Voltage |  | V | float
5002 | 1#battery bank | Bank Current |  | A | float
5004 | 1#battery bank | Bank SOC |  | % | float
5006 | 1#battery bank | Bank SOH |  | % | float
5008 | 1#battery bank | Bank Insulation Resistance |  | Ω | float | Empty point position annotation
5010 | 1#battery bank | Bank Available Charge Energy |  | kWh | float
5012 | 1#battery bank | Bank Available Discharge Energy |  | kWh | float
5014 | 1#battery bank | System Allowed Maximum Charge Current |  | A | float | System Allowed Maximum Charge Power = Maximum Charge Current * Bank Voltage；
5016 | 1#battery bank | System Allowed Maximum Discharge Current |  | A | float | System Allowed Maximum Discharge Power = Maximum Discharge Current * Bank Voltage；
5018 | 1#battery bank | Today’s Charge Energy |  | kWh | float
5020 | 1#battery bank | Today’s Discharge Energy |  | kWh | float
5022 | 1#battery bank | Accumulated Charge Energy |  | kWh | float
5024 | 1#battery bank | Accumulated Discharge Energy |  | kWh | float
...
5100 | 2#battery bank | Bank Voltage |  | V | float
...
9900 | 50#battery bank | Bank Voltage |  | V | float
...

## Rack and Cell Information
LC Information -- EMS Read from LC
Register Settings (Modbus Addr:N+1 Function Code:0x04 - Read Input Registers)
Modbus Addr (ID) : N+1,(e.g.，rack#1，set device addr to 2）
Notes： 1、All values do not require scaling or adding offset. For example: Measurement point address 1, measurement value 456.7 represents Rack voltage of 456.7V.
Addr | Equipment | Name | Accuracy | Cell | Type | Notes
0 | X# Rack | Number of cells in Rack |  |  | u16 | Maximum 1000 V6 Update Content
1 | X# Rack | Rack Voltage |  | V | float
3 | X# Rack | Rack Current |  | A | float
5 | X# Rack | Rack SOC |  | % | float
7 | X# Rack | Rack SOH |  | % | float
9 | X# Rack | Rack Insulation Resistance |  | Ω | float
11 | X# Rack | Maximum Allowable Charge Current |  | A | float
13 | X# Rack | Maximum Allowable Discharge Current |  | A | float
15 | X# Rack | Total Charge Energy |  | kWh | float
17 | X# Rack | Total Discharge Energy |  | kWh | float
19 | X# Rack | Available Charge Energy |  | kWh | float
21 | X# Rack | Available Discharge Energy |  | kWh | float
23 | X# Rack | Average Cell Voltage |  | V | float
25 | X# Rack | Average Cell Temperature |  | ℃ | float
27 | X# Rack | Maximum Cell Voltage |  | V | float
29 | X# Rack | Maximum Cell Voltage Cell Number |  | 1 | float
31 | X# Rack | Minimum Cell Voltage |  | V | float
33 | X# Rack | Minimum Cell Voltage Cell Number |  | 1 | float
35 | X# Rack | Maximum Cell Temperature |  | ℃ | float
37 | X# Rack | Maximum Cell Temperature Cell Number |  | 1 | float
39 | X# Rack | Minimum Cell Temperature |  | ℃ | float
41 | X# Rack | Minimum Cell Temperature Cell Number |  | 1 | float
43 | X# Rack | Maximum Cell SOC |  | % | float
45 | X# Rack | Maximum Cell SOC Cell Number |  | 1 | float
47 | X# Rack | Minimum Cell SOC |  | % | float
49 | X# Rack | Minimum Cell SOC Cell Number |  | 1 | float
51 | X# Rack | Maximum Cell SOH |  | % | float
53 | X# Rack | Maximum Cell SOH Cell Number |  | 1 | float
55 | X# Rack | Minimum Cell SOH |  | % | float
57 | X# Rack | Minimum Cell SOH Cell Number |  | 1 | float
...
100 | 1# Cell | Cell Voltage |  | V | float
102 | 1# Cell | Cell Temperature |  | ℃ | float
104 | 1# Cell | Cell SOC |  | % | float
106 | 1# Cell | Cell SOH |  | % | float
108 | 1# Cell | Cell Resistance |  | Ω | float
110 | 2# Cell | Cell Voltage |  | V | float
...
10090 | 1000# Cell | Cell Voltage |  | V | float
...

## Liquid Cooling Information
LC Information -- EMS Read from LC
Register Settings (Modbus Addr:1 Function Code:0x04 - Read Input Registers)
Modbus Addr (ID) : 1
Notes： 1、Ensure that each read operation is limited to data from at most one device.
Addr | Equipment | Name | Accuracy | Unit | Type | Notes
30000 | 1#Liquid Cooling | Operating Status |  |  | u16 | 0：Stopped，1：Running
30001 | 1#Liquid Cooling | Reserve |  |  | u16
30002 | 1#Liquid Cooling | Reserve |  |  | u16
30003 | 1#Liquid Cooling | Reserve |  |  | u16
30004 | 1#Liquid Cooling | Operating Mode |  |  | u16 | 0：Stopped，1：Cooling， 2：Heating， 3：Self-circulation， 4：Automatic， 5：Standby
30006 | 1#Liquid Cooling | Ambient Temperature | 0.1 | ℃ | float
30008 | 1#Liquid Cooling | Supply Water Temperature | 0.1 | ℃ | float
30010 | 1#Liquid Cooling | Inlet Water Temperature | 0.1 | ℃ | float
30012 | 1#Liquid Cooling | Supply Water Pressure |  |  | float
30014 | 1#Liquid Cooling | Return Water Pressure |  |  | float
30016 | 1#Liquid Cooling | Fan Operating Status |  |  | u16
30017 | 1#Liquid Cooling | Water Pump Operating Status |  |  | u16
30018 | 1#Liquid Cooling | Electric Heating Operating Status |  |  | u16
30019 | 1#Liquid Cooling | Refrigerant Operating Status |  |  | u16
30020 | 1#Liquid Cooling | Fan Output |  |  | float | Empty point position annotation
30022 | 1#Liquid Cooling | Water Pump Output |  |  | float
30024 | 1#Liquid Cooling | Target Cooling Start Point | 0.1 | ℃ | float
30026 | 1#Liquid Cooling | Target Cooling Stop Point | 0.1 | ℃ | float
30028 | 1#Liquid Cooling | Target Heating Start Point | 0.1 | ℃ | float
30030 | 1#Liquid Cooling | Target Heating Stop Point | 0.1 | ℃ | float
30032 | 1#Liquid Cooling | EMS Control Mode Status |  |  | u16 | 0：false，1：true
...
...
30040 | 2#Liquid Cooling | Operating Status |  |  | u16
...
...
33960 | 100#Liquid Cooling | Operating Status |  |  | u16

## DIO Information
LC Information -- EMS Read from LC
Register Settings (Modbus Addr:1 Function Code:0x04 - Read Input Registers)
Modbus Addr (ID) : 1
Notes： 1、All values do not require scaling or adding offset. 2、Ensure that each read operation is limited to data from at most one device.
Addr | Equipment | Name | Accuracy | Unit | Type | Notes
20000 | 1#DIO | Reserve |  |  | u16 | Empty point position annotation
20001 | 1#DIO | Reserve |  |  | u16
20002 | 1#DIO | Reserve |  |  | u16
20003 | 1#DIO | Reserve |  |  | u16
20004 | 1#DIO | Reserve |  |  | u16
20005 | 1#DIO | Reserve |  |  | u16
20006 | 1#DIO | 1#DI-1（crash-stop） |  |  | u16 | 0: normal ； 1: Alarm
20007 | 1#DIO | 1#DI-2（Surge fault feedback） |  |  | u16 | 0: normal ； 1: Alarm
20008 | 1#DIO | 1#DI-3（PCS Discharge/Charge Status） |  |  | u16 | 0: normal ； 1: Alarm
20009 | 1#DIO | 1#DI-4（Water Cooling） |  |  | u16 | 0: normal ； 1: Alarm
20010 | 1#DIO | 1#DI-5（Aerosol spraying） |  |  | u16 | 0: normal ； 1: Alarm
20011 | 1#DIO | 1#DI-6（KA1-KA6 Contactor Monitoring） |  |  | u16 | 0: normal ； 1: Alarm
20012 | 1#DIO | 1#DI-7（Reserve） |  |  | u16
20013 | 1#DIO | 1#DI-8（Reserve） |  |  | u16
20014 | 1#DIO | 1#DI-9（Temperature feedback） |  |  | u16 | 1: normal ； 0: Alarm
20015 | 1#DIO | 1#DI-10（Smoke feedback） |  |  | u16 | 1: normal ； 0: Alarm
20016 | 1#DIO | 1#DI-11（AC side entrance guard） |  |  | u16 | 1: normal ； 0: Alarm
20017 | 1#DIO | 1#DI-12（DC side entrance guard） |  |  | u16 | 1: normal ； 0: Alarm
20018 | 1#DIO | 1#DI-13（Exhaust Fan Feedback） |  |  | u16 | 1: normal ； 0: Alarm
20019 | 1#DIO | 1#DO-1（Running Indicator） |  |  | u16 | 0: Off, 1: On
20020 | 1#DIO | 1#DO-2（Fault Indicator） |  |  | u16 | 0: Off, 1: On
20021 | 1#DIO | 1#DO-3（Intermediate relay） |  |  | u16 | 0: Off, 1: On
...
20022 | 2#DIO | Reserve |  |  | u16
20024 | 2#DIO | Reserve |  |  | u16
20025 | 2#DIO | Reserve |  |  | u16
20026 | 2#DIO | Reserve |  |  | u16
20027 | 2#DIO | Reserve |  |  | u16
20028 | 2#DIO | Reserve |  |  | u16
20029 | 2#DIO | 2#DI-1 |  |  | u16
20030 | 2#DIO | 2#DI-2 |  |  | u16
20031 | 2#DIO | 2#DI-3 |  |  | u16
20032 | ...
20033 | 2#DIO | 2#DO-1 |  |  | u16
20034 | 2#DIO | 2#DO-2 |  |  | u16
20035 | 2#DIO | 2#DO-3 |  |  | u16
20036 | ...
20037 | 50#DIO | Reserve |  |  | u16
20038 | 50#DIO | Reserve |  |  | u16
20039 | 50#DIO | Reserve |  |  | u16
20040 | 50#DIO | Reserve |  |  | u16
20041 | 50#DIO | Reserve |  |  | u16
20042 | 50#DIO | Reserve |  |  | u16
20043 | 50#DIO | 50#DI-1 |  |  | u16

## Meter Information
LC Information -- EMS Read from LC
Register Settings (Modbus Addr:1 Function Code:0x04 - Read Input Registers)
Modbus Addr (ID) : 1
Notes： 1、All values do not require scaling or adding offset. For example: Measurement point address 10000, measurement value 123.4 represents Total Forward Active Energy of 123.4kWh. 2、Ensure that each read operation is limited to data from at most one device.
Addr | Equipment | Name | Accuracy | Unit | Type | Notes
10000 | 1#Bidirectional Meter | Total Forward Active Energy |  | kWh | float | Empty point position annotation
10002 | 1#Bidirectional Meter | Total Forward Sharp Energy |  | kWh | float
10004 | 1#Bidirectional Meter | Total Forward Peak Energy |  | kWh | float
10006 | 1#Bidirectional Meter | Total Forward Flat Energy |  | kWh | float
10008 | 1#Bidirectional Meter | Total Forward Valley Energy |  | kWh | float
10010 | 1#Bidirectional Meter | Total Reverse Active Energy |  | kWh | float
10012 | 1#Bidirectional Meter | Total Reverse Sharp Energy |  | kWh | float
10014 | 1#Bidirectional Meter | Total Reverse Peak Energy |  | kWh | float
10016 | 1#Bidirectional Meter | Total Reverse Flat Energy |  | kWh | float
10018 | 1#Bidirectional Meter | Total Reverse Valley Energy |  | kWh | float
10020 | 1#Bidirectional Meter | Total Active Power |  | kW | float
...
10050 | 2#Bidirectional Meter | Total Forward Active Energy |  | kWh | float
...
14950 | 100#Bidirectional Meter | Total Forward Active Energy |  | kWh | float
...

## Air Conditioning Information
LC Information -- EMS Read from LC
Register Settings (Modbus Addr:1 Function Code:0x04 - Read Input Registers)
Modbus Addr (ID) : 1
Notes： 1、All values do not require scaling or adding offset. For example: Measurement point address 15004, measurement value 22.4 represents Cooling Low Point of 22.4°c. 2、Ensure that each read operation is limited to data from at most one device.
Addr | Equipment | Name | Accuracy | Unit | Type | Notes
15000 | 1#AC | Operating Status |  |  | u16 | 0：Stopped，1：Running
15001 | 1#AC | Reserve |  |  | u16
15002 | 1#AC | Reserve |  |  | u16
15003 | 1#AC | Reserve |  |  | u16
15004 | 1#AC | Cooling Low Point | 0.1 | °c | float
15006 | 1#AC | Cooling High Point | 0.1 | °c | float
15008 | 1#AC | Heating Low Point | 0.1 | °c | float
15010 | 1#AC | Heating High Point | 0.1 | °c | float
15012 | 1#AC | Dehumidification High Point (Start Point) | 0.1 |  | float
15014 | 1#AC | Dehumidification Low Point (Stop Point) | 0.1 |  | float
15016 | 1#AC | High Temperature Alarm Point | 0.1 | °c | float
15018 | 1#AC | Low Temperature Alarm Point | 0.1 | °c | float
15020 | 1#AC | Temperature | 0.1 | °c | float
15022 | 1#AC | Temperature Status |  |  | u16 | 0: normal ； 1: Alarm
15023 | 1#AC | Voltage Status |  |  | u16 | 0: normal ； 1: Alarm
15024 | 1#AC | Sensor Status |  |  | u16 | 0: normal ； 1: Alarm
15025 | 1#AC | Compressor Status |  |  | u16 | 0: normal ； 1: Alarm
15026 | 1#AC | Air Pressure Status |  |  | u16 | 0: normal ； 1: Alarm
15027 | 1#AC | Relative Humidity | 0.1 |  | float
...
15050 | 2#AC | Operating Status |  |  | u16 | 0：Stopped，1：Running
15051 | 2#AC | Reserve |  |  | u16
15052 | 2#AC | Reserve |  |  | u16
15053 | 2#AC | Reserve |  |  | u16
...
19950 | 100#AC | Operating Status |  |  | u16 | 0：Stopped，1：Running
19951 | 100#AC | Reserve |  |  | u16
19952 | 100#AC | Reserve |  |  | u16
19953 | 100#AC | Reserve |  |  | u16
...

## PV Information
LC Information -- EMS Read from LC
Register Settings (Modbus Addr:1 Function Code:0x04 - Read Input Registers)
Modbus Addr (ID) : 1
Notes： 1、All values do not require scaling or adding offset. For example: Measurement point address 25016, measurement value 123.4 represents Total AC Active Power of 123.4 kW. 2、Ensure that each read operation is limited to data from at most one device.
Addr | Equipment | Name | Accuracy | Unit | Type | Notes
25000 | 1#PV | Operating Status |  |  | u16 | 0：Stopped，1：Running
25001 | 1#PV | Reserve |  |  | u16 | Empty point position annotation
25002 | 1#PV | AC Phase A Voltage | 0.1 | V | float
25004 | 1#PV | AC Phase B Voltage | 0.1 | V | float
25006 | 1#PV | AC Phase C Voltage | 0.1 | V | float
25008 | 1#PV | AC Phase A Current | 0.1 | A | float
25010 | 1#PV | AC Phase B Current | 0.1 | A | float
25012 | 1#PV | AC Phase C Current | 0.1 | A | float
25014 | 1#PV | AC Frequency | 0.01 | Hz | float
25016 | 1#PV | Total AC Active Power | 0.1 | kW | float | “+”：charge，“-”：discharge
25018 | 1#PV | Total AC Reactive Power | 0.1 | kvar | float
25020 | 1#PV | Total AC Apparent Power | 0.1 | kvar | float
25022 | 1#PV | Total AC Power Factor | 0.01 |  | float
25024 | 1#PV | Phase A AC Active Power | 0.1 | kW | float
25026 | 1#PV | Phase B AC Active Power | 0.1 | kW | float
25028 | 1#PV | Phase C AC Active Power | 0.1 | kW | float
25030 | 1#PV | Phase A AC Reactive Power | 0.1 | kvar | float
25032 | 1#PV | Phase B AC Reactive Power | 0.1 | kvar | float
25034 | 1#PV | Phase C AC Reactive Power | 0.1 | kvar | float
25036 | 1#PV | Phase A AC Apparent Power | 0.1 | kVA | float
25038 | 1#PV | Phase B AC Apparent Power | 0.1 | kVA | float
25040 | 1#PV | Phase C AC Apparent Power | 0.1 | kVA | float
25042 | 1#PV | Phase A AC Power Factor | 0.01 |  | float
25044 | 1#PV | Phase B AC Power Factor | 0.01 |  | float
25046 | 1#PV | Phase C AC Power Factor | 0.01 |  | float
25048 | 1#PV | IGBT Module Temperature | 0.1 | ℃ | float
25050 | 1#PV | Ambient Temperature | 0.1 | ℃ | float
25052 | 1#PV | Total AC Charging Energy | 0.1 | kWh | float
25054 | 1#PV | Total AC Discharging Energy | 0.1 | kWh | float
25056 | 1#PV | Daily AC Charging Energy | 0.1 | kWh | float
25058 | 1#PV | Daily AC Discharging Energy | 0.1 | kWh | float
25060 | 1#PV | Number of branches | 1 | 1 | u32
25062 | 1#PV | Branch 1 DC Power | 0.1 | kW | float
25064 | 1#PV | Branch 1 DC Voltage | 0.1 | V | float
25066 | 1#PV | Branch 1 DC Current | 0.1 | A | float
25068 | 1#PV | Branch 2~n DC Power | 0.1 | kW | float
25070 | 1#PV | Branch 2~n DC Voltage | 0.1 | V | float
25072 | 1#PV | Branch 2~n DC Current | 0.1 | A | float
...
...
...
25100 | 2#PV | Operating Status |  |  | u16 | 0：Stopped，1：Running
25101 | 2#PV | Reserve |  |  | u16
25102 | 2#PV | AC Phase A Voltage | 0.1 | V | float
...
29900 | 50#PV | Operating Status |  |  | u16 | 0：Stopped，1：Running
29901 | 50#PV | Reserve |  |  | u16
29902 | 50#PV | AC Phase A Voltage | 0.1 | V | float

## Project Reservation
Addr | Equipment | Name | Accuracy | Unit | Type | Notes
50000 | [5 empty] | Reserved, flexible allocation in actual projects
...
65536 | [5 empty] | Reserved, flexible allocation in actual projects