## 3E-input
3E Indicator | Display Name on SynaptiQ | Description | Device level (blue= BESS measures, Light Green = Inverter level, Dark Green = Meter level, Yellow = Sensor level, Orange = Trackers measures) | Unit | Priority (1 = Highest) | PM DefFile 'Inverter' | PM DefFile 'Meter' | PM DefFile 'Battery' | PM DefFile 'Sensor'
charge.state | State of Charge | Percentage of charge of the storage device | BESS | % | 1 |  |  | B_SoC
charge.health | State of Health | State of health of the storage device | BESS | % | 2 |  |  | B_SoH
charge.meter.ac | Energy AC Charging | Positive AC yield pertinent to the charge of the device | BESS | kWh | 2
charge.meter.dc | Energy DC Charging | Positive DC yield pertinent to the charge of the device | BESS | kWh | 2
temperature.battery | Temperature Battery | Temperature of a battery. | BESS | °C | 2 |  |  | B_TEMP
voltage.battery | Voltage Battery | Voltage of a battery. | BESS | V | 2 |  |  | B_U_DC
charge.state.error | State of Charge Error | Tolerance of accuracy regarding the state of charge | BESS | % | 3
charge.voltage.set.point | Voltage DC Charging | DC voltage setpoint that the storage system targets | BESS | V | 3
mode.errorCode | Error code | The error code reported by a device. | Inverter | / | 1
mode.statusCode | Status code | The status code reported by a device. | Inverter | / | 1
resistance.isolation | Resistance Isolation | RISO | Inverter | Ohm | 1 | R_ISO
temperature.inverter | Temperature Inverter | Temperature of the Inverter | Inverter | °C | 1 | TEMP_INT
yield.inverter | Energy | AC Energy production calculated based on the data provided by the generation system and the imported historical data. | Inverter | Wh | 1 | E_TOT
current.ac | Current AC | Total AC current outputted from the inverter | Inverter/Meter | A | 1 | I_AC
current.ac.AC1 | Current AC Phase 1 | Phase 1 AC current | Inverter/Meter | A | 1 | I_AC[1..3] | M_I_AC_[1..3]
current.ac.AC2 | Current AC Phase 2 | Phase 2 AC current | Inverter/Meter | A | 1 | I_AC[1..3] | M_I_AC_[1..3]
current.ac.AC3 | Current AC Phase 3 | Phase 3 AC current | Inverter/Meter | A | 1 | I_AC[1..3] | M_I_AC_[1..3]
current.dc | Current DC | Total DC-side current | Inverter/Meter | A | 1 | I_DC
current.dc.DCX | Current DC Input X | Current DC at input X | Inverter/Meter | A | 1 | I_DC_MPPT_[1..X]
energy.generation | Energy Generation | AC energy generated by the generators without considering AC losses. | Inverter/Meter | kWh | 1
energy.production | Energy Production | AC energy produced by a generator or aggregate as input to a next level of aggregation with AC losses considered up to this level. | Inverter/Meter | kWh | 1
frequency | Frequency Grid | Frequency of the Grid/Inverter | Inverter/Meter | Hz | 1 | FREQ | M_FREQ
frequency.AC1 | Frequency Grid Phase 1 | Frequency on Phase 1 | Inverter/Meter | Hz | 1 | FREQ[1..3] | M_FREQ_[1..3]
frequency.AC2 | Frequency Grid Phase 2 | Frequency on Phase 2 | Inverter/Meter | Hz | 1 | FREQ[1..3] | M_FREQ_[1..3]
frequency.AC3 | Frequency Grid Phase 3 | Frequency on Phase 3 | Inverter/Meter | Hz | 1 | FREQ[1..3] | M_FREQ_[1..3]
power.ac | Power AC | Active AC Power. | Inverter/Meter | W | 1 | P_AC | M_P_AC
power.ac.AC1 | Power AC Phase 1 | Active AC Power at Phase 1 | Inverter/Meter | W | 1 | P_AC[1..3] | M_P_AC_[1..3]
power.ac.AC2 | Power AC Phase 2 | Active AC Power at Phase 2 | Inverter/Meter | W | 1 | P_AC[1..3] | M_P_AC_[1..3]
power.ac.AC3 | Power AC Phase 3 | Active AC Power at Phase 3 | Inverter/Meter | W | 1 | P_AC[1..3] | M_P_AC_[1..3]
power.ac.setpoint | Power AC - setpoint | Setpoint for the power AC | Inverter/Meter | W | 1 | cmd_P_AC_setabs
power.dc | Power DC | DC Power. | Inverter/Meter | W | 1 | P_DC
power.dc.DCX | Power DC input X | Power DC at input X | Inverter/Meter | W | 1 | P_DC[1..x]
power.factor.displacement | Cosinus Phi | COS PHI | Inverter/Meter | / | 1 | PF
power.factor.setpoint | Power Factor - setpoint | Setpoint for the power factor | Inverter/Meter | / | 1 | cmd_PF
power.factor.true | Power Factor | Power Factor | Inverter/Meter | / | 1 | PF | M_PF
power.factor.true.AC1 | Power Factor Phase 1 | Power Factor at phase 1 | Inverter/Meter | / | 1 | PF_[1..3] | M_PF_[1..3]
power.factor.true.AC2 | Power Factor Phase 2 | Power Factor at phase 2 | Inverter/Meter | / | 1 | PF_[1..3] | M_PF_[1..3]
power.factor.true.AC3 | Power Factor Phase 3 | Power Factor at phase 3 | Inverter/Meter | / | 1 | PF_[1..3] | M_PF_[1..3]
power.VA | Power VA | VA = volt·ampere, Apparent AC Power | Inverter/Meter | kVA | 1 | S_AC
power.var | Power var | var = volt·ampere reactive, Reactive AC Power | Inverter/Meter | kVAr | 1 | Q_AC
voltage.ac | Voltage AC | Voltage between a single phase and neutral or the average phase to neutral over all phases. | Inverter/Meter | V | 1
voltage.ac.AC1 | Voltage AC Phase 1 | Voltage between phase 1 and neutral | Inverter/Meter | V | 1
voltage.ac.AC2 | Voltage AC Phase 2 | Voltage between phase 2 and neutral | Inverter/Meter | V | 1
voltage.ac.AC3 | Voltage AC Phase 3 | Voltage between phase 3 and neutral | Inverter/Meter | V | 1
voltage.ac.ab | Voltage AC 1-2 | Line voltage between phases L1 and L2 | Inverter/Meter | V | 1 | U_AC[1..3] | M_U_AC_ [1..3]
voltage.ac.bc | Voltage AC 2-3 | Line voltage between phases L2 and L3 | Inverter/Meter | V | 1 | U_AC[1..3] | M_U_AC_ [1..3]
voltage.ac.ca | Voltage AC 3-1 | Line voltage between phases L3 and L1 | Inverter/Meter | V | 1 | U_AC[1..3] | M_U_AC_ [1..3]
voltage.dc | Voltage DC | Voltage DC | Inverter/Meter | V | 1 | U_DC
voltage.dc.DCX | Voltage DC Input X | Voltage DC at input X | Inverter/Meter | V | 1 | U_DC_MPPT_[1..x]
derated.capacity | Power Limitation Normalized | Normalized active power limitation setpoint, same as [derated.power.ac] / [capacity.rated.ac]. | Inverter/Meter | % | 2
derated.power.ac | Power AC Limit | The maximum value for [power.ac] as imposed by external constraints. When no constraints apply, the value is the same as [capacity.rated.ac]. | Inverter/Meter | W | 2
energy.ac.counter | Energy Counter | Energy counter value as reported by the device normalised to kWh. | Inverter/Meter | kWh | 2
energy.ac.daily | Energy Daily | Energy daily counter value as reported by the device normalised to kWh. | Inverter/Meter | kWh | 2
power.var.setpoint | Power var - setpoint | Setpoint for the reactive power | Inverter/Meter | kVAr | 2
yield.dc | Energy DC | Energy measured at DC level. | Inverter/Meter | Wh | 2
current.ac.ground | Current AC Ground | Current measured through the grounding conductor | Inverter/Meter | A | 3
current.ac.neutral | Current AC Neutral | Current measured through neutral | Inverter/Meter | A | 3
current.ac.thd | Current AC THD | Total harmonic distortion of AC current | Inverter/Meter | % | 3
current.ac.unbalance | Current AC Unbalance | Maximum difference of the AC phases compared to average | Inverter/Meter | A | 3
current.apparent | Current AC Apparent | Apparent component of the total AC current | Inverter/Meter | A | 3
energy.vah | Energy VAh | VAh = Volt·Ampere hour, Apparent AC Energy | Inverter/Meter | kVAh | 3
energy.varh | Energy varh | varh = volt·ampere reactive hour, Reactive AC Energy | Inverter/Meter | kVArh | 3
energy.varh.capacitive | Energy varh capacitive | varh = volt·ampere reactive capacitive hour, Reactive Capacitive AC Energy | Inverter/Meter | kVArh | 3
energy.varh.daily | Energy varh Daily | Daily counter for [energy.varh]. | Inverter/Meter | kVArh | 3
energy.varh.import | Energy varh Import | varh = volt·ampere reactive hour, Reactive AC Energy imported. | Inverter/Meter | kVArh | 3
energy.varh.inductive | Energy varh inductive | varh = volt·ampere reactive inductive hour, Reactive Inductive AC Energy | Inverter/Meter | kVArh | 3
energy.varh.q1 | Energy varh Q1 | varh = volt·ampere reactive hour in Quadrant 1 (import active/import reactive) | Inverter/Meter | kVArh | 3
energy.varh.q2 | Energy varh Q2 | varh = volt·ampere reactive hour in Quadrant 2 (export active/import reactive) | Inverter/Meter | kVArh | 3
energy.varh.q3 | Energy varh Q3 | varh = volt·ampere reactive hour in Quadrant 3 (export active/export reactive) | Inverter/Meter | kVArh | 3
energy.varh.q4 | Energy varh Q4 | varh = volt·ampere reactive hour in Quadrant 4 (import active/export reactive) | Inverter/Meter | kVArh | 3
impedance | Impedance Grid | Impedance from the Grid | Inverter/Meter | Ohm | 3
power.var.capacitive | Power var capacitive | var = volt·ampere reactive capacitive, Reactive Capacitive AC Power | Inverter/Meter | kVAr | 3
power.var.inductive | Power var inductive | var = volt·ampere reactive inductive, Reactive Inductive AC Power | Inverter/Meter | kVAr | 3
temperature.enclosure | Temperature Enclosure | Air temperature inside a device enclosure, e.g., a cabinet. | Inverter/Meter/Sensor | °C | 1
mode.flag | Flag state | The state of a flag, i.e., a value of 1 means on/up/active and a value of 0 means off/down/normal. | Inverter/Meter/Sensor/Tracker | / | 2
energy.export | Energy Export | AC energy exported to the grid, always positive. | Meter | kWh | 1 |  | M_E_EXP
energy.import | Energy Import | AC energy imported from the grid, always positive. | Meter | kWh | 1 |  | M_E_IMP
yield.meter.green | Energy (Meter) | AC energy balance of the generation system. The balance may be negative due to energy consumption by the generation system. | Meter | Wh | 1 |  | M_E
energy.consumption | Energy Consumption | Local energy consumption which is not related to the generation system. | Meter | kWh | 2
energy.consumption.import | Energy Grid-Consumption | The part of [energy.consumption] that was imported from the grid. | Meter | kWh | 2
energy.consumption.self | Energy Self-Consumption | The part of [energy.consumption] that was produced by the generation system. | Meter | kWh | 2
energy.system | Energy System | AC energy consumed by the generation system. | Meter | kWh | 3
power.ac.import | Power AC Import | Active AC Power import. | Meter | W | 3
voltage.tap | Voltage tap | Tap position in transformer. | Meter | / | 3
derated.capacity | Power Limitation Normalized | Normalized active power limitation setpoint, same as [derated.power.ac] / [capacity.rated.ac]. | Sensor | % | 1
irradiance | Irradiance | Irradiance in the plane of the array(s) calculated using the same configuration and data as [irradiation.actual]. | Sensor | W/m² | 1 |  |  |  | S_POA
irradiance.horizontal | Irradiance Horizontal | irradiance in the horizontal plane | Sensor | W/m² | 1 |  |  |  | S_GHI
temperature.ambient | Temperature Ambient | Ambient temperature | Sensor | °C | 1 |  |  |  | S_TEMP_AMB
temperature.cells | Temperature PV Module | Temperature of PV cells. | Sensor | °C | 1 |  |  |  | S_TEMP_CELL
fraction.loss.soiling | Fraction Soling Loss | The fraction of total performance lost due to soiling transmission loss. | Sensor | % | 2
humidity.relative | Relative humidity | Relative humidity | Sensor | % | 2
index.loss.soiling | Index Loss Soiling | The ratio of soiled to clean performance (1 - [fraction.loss.soiling]). | Sensor | % | 2
precipitation.height | Precipitation | Amount of rainfall during the interval. | Sensor | mm | 2
precipitation.height.accumulated | Snowfall | Accumulated snowfall. | Sensor | cm | 2
precipitation.mass.load | Snowload | Snow mass per unit of surface | Sensor | mm | 2
pressure.air | Pressure Air | Air pressure | Sensor | hpa | 2
temperature.oil | Temperature Oil | Transformer oil temperature | Sensor | °C | 2
temperature.winding | Temperature Winding | Transformer winding temperature | Sensor | °C | 2
wind.bearing | Wind Bearing | Angle of incidence of the wind at instant t | Sensor | ° | 2
wind.speed | Wind Speed | Speed of the wind at instant t | Sensor | m/s | 2
flow.water | Flow water | Flow of water as volume per unit of time. | Sensor | m³/s | 3
fraction.cleaned | Fraction cleaned | Fraction of cleaned items vs total number. | Sensor | % | 3
fraction.open | Fraction Open | Opening of a valve or other device as percentage of completely open. | Sensor | % | 3
irradiance.diffuse | Irradiance Diffuse | irradiance diffuse | Sensor | W/m² | 3
level.gate | Level Gate | Opening of a gate as distance. | Sensor | cm | 3
level.oil | Level Oil | Level of oil. | Sensor | cm | 3
level.water | Level Water | Level of water. | Sensor | cm | 3
temperature.igbt | Temperature IGBT | Temperature of the IGBT component. | Sensor | °C | 3
temperature.mosfet | Temperature MOSFET | Temperature of the MOSFET component. | Sensor | °C | 3
angle.axis1 | Angle axis 1 | Angle of first axis. | Tracker | ° | 1
angle.axis1.setpoint | Angle axis 1 - setpoint | Setpoint for angle of first axis. | Tracker | ° | 1
angle.axis2 | Angle axis 2 | Angle of second axis. | Tracker | ° | 1
angle.axis2.setpoint | Angle axis 2 - setpoint | A setpoint for angle of second axis. | Tracker | ° | 1
angle.axis1.error | Angle axis 1 - error | Difference between angle and set-point of first axis. | Tracker | ° | 3
angle.axis2.error | Angle axis 2 - error | Difference between angle and set-point of second axis. | Tracker | ° | 3
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Eric Bonilla Minguillon (3E) do you know what is this measurement? If yes, could you define it? Reply: I guess it refers to the difference of charge.state and charge.state.setpoint. But I wouldn't consider this a big deal.

## TAG_INVERTER
Tags | Previous Tags | Description | MVP | Feature | Function | Column1
SERIAL | DisplaySerial / DisplaySerialNumber | Serial Number of inverter | x | 1-BasicInfo
MODEL | DisplayModel | Model of inverter | x | 1-BasicInfo
MANUFACTURER | ManufacturerStr | Manufacturer of inverter |  | 1-BasicInfo
NAME |  | Name of inverter |  | 1-BasicInfo | A VOIR : PAS DANS LE FICHIER DE DEF
P_RATED | NominalPower | Nominal Active Power | x | 1-BasicInfo | getInfo()
Q_RATED |  | Nominal Reactive Power |  | 1-BasicInfo | getInfo()
STATE[1..x] |  |  |  | 2-Basic Status
ALARM[1..x] |  |  |  | 2-Basic Status
CMD_ON | cmdOn | Active High Switch | x | 3-BasicControl | start() / stop()
CMD_OFF | cmdOff | Active Low Switch | x | 3-BasicControl | start() / stop()
CMD_P_AC_LIM_PERCENT |  | Active Power Limitation in percent | x | 4-ActiveControl | setACLimitPercent() / setACLimitkW() /getACLimitPercent()/getACLimitKw()
CMD_P_AC_LIM_ABS |  | Active Power Limitation (in unit specified in def file : W, kW ...) |  | 4-ActiveControl | setACLimitPercent() / setACLimitkW() /getACLimitPercent()/getACLimitKw()
CMD_P_AC_SET_PERCENT | cmdPwrPercent | Active Power Setpoint in percent | x | 4-ActiveControl | setACPercent() / setkW() /getACPercent()/getACKw()
CMD_P_AC_SET_ABS | cmdPwr | Active Power Setpoint (in unit specified in def file : W, kW ...) | x | 4-ActiveControl | setACPercent() / setkW() /getACPercent()/getACKw()
CMD_P_ENA | WMaxLim_Ena | Power Limitation Enable Latch | x | 4-ActiveControl/Init | setACLimitPercent() / setACLimitkW() /getACLimitPercent()/getACLimitKw()
CMD_P_MODE |  | Selection mode de pilotage de l'actif
CMD_RAMP_TIME_S | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | x | 4-ActiveControl/Init | TBD setRamp etc…
CMD_REVERT_TIME_S | WMaxLimPct_RvrtTms | Timeout period for power limit. | x | 4-ActiveControl/Init | TBD setRamp etc…
VAR_P_AC_REPEAT_TIME_S |  | Repeating time for P_AC control |  | 4-ActiveControl/Init | Constant in def file : repeating period for power control
CMD_Q_AC_LIM_PERCENT |  | Reactive Power Limitation in percent |  | 5-ReactiveControl | idem RC
CMD_Q_AC_LIM_ABS |  | Reactive Power Limitation (in unit specified in def file : VAR, kVAR ...) |  | 5-ReactiveControl | idem RC
CMD_Q_AC_SET_PERCENT |  | Reactive Power Setpoint in percent |  | 5-ReactiveControl | idem RC
CMD_Q_AC_SET_ABS |  | Reactive Power Setpoint (in unit specified in def file : VAR, kVAR ...) |  | 5-ReactiveControl | idem RC
CMD_Q_ENA | VArPct_Ena | Activation consigne reactif
CMD_Q_MODE | VArPct_Mod | Selection mode de pilotage du réactif
CMD_Q_RAMP_TIME_S | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | x | 4-ActiveControl/Init | TBD setRamp etc…
CMD_Q_REVERT_TIME_S | VArPct_RvrtTms | Timeout period for power limit. | x | 4-ActiveControl/Init | TBD setRamp etc…
CMD_PF_INT | cmdPFint
CMD_Q_PERCENT | cmdQPct
CMD_Q_ANGLE | cmdAngle
VAR_PF_SIGN |  | Indication du signe du facteur de puissance
CMD_PF | cmdPF;OutPFSet | Power Factor Setpoint | x | 5-ReactiveControl | TBD
E_DAY | EnergyDay | Daily Energy Generation | x | 6-BasicMonitoring | getEnergy()
E_TOT | EnergyTotal | Total Energy Generation | x | 6-BasicMonitoring | getEnergy()
TOT |  | Total Operating Time |  | 6-BasicMonitoring | getStatus()
TEMP_INT |  | Internal Temperature | x | 6-BasicMonitoring | getStatus()
S_AC |  | Total Apparent Power |  | 7-ACMonitoring | getApparentPower()
S_AC_[1..3] |  | Apparent Power Phase 1..3 |  | 7-ACMonitoring | getApparentPower()
P_AC | RealPower | Total Active Power | x | 7-ACMonitoring | getActivePower() | getActivePower()
P_AC_[1..3] |  | Active Power phase 1..3 | x | 7-ACMonitoring | getActivePower() | getActivePower()
PF_[1..3] |  | Power Factor Phase 1..3 | x | 7-ACMonitoring | getPowerFactor()
PF | cosPHI / CosPhi | Power Factor | x | 7-ACMonitoring | getPowerFactor()
Q_AC | ReactivePower | Total Reative Power | x | 7-ACMonitoring | getReactivePower()
Q_AC_[1..3] |  | Reactive Power Phase 1..3 | x | 7-ACMonitoring | getReactivePower()
FREQ_[1..3] | GridFrequency1-2-3 | Grid Frequency Phase 1..3 | x | 7-ACMonitoring | getLine()
FREQ | GridFrequency | Grid Frequency | x | 7-ACMonitoring | getLine()
I_AC |  | AC Current | x | 7-ACMonitoring | getLine()
I_AC_[1..3] |  | AC Current Phase 1..3 | x | 7-ACMonitoring | getLine()
U_AC_L1L2 - L2L3 - L3L1 |  | AC Phase to phase Voltage | x | 7-ACMonitoring | getLine()
U_AC_[1..3] |  | AC Phase to neutral Voltage 1..3 | x | 7-ACMonitoring | getLine()
I_DC |  | DC Bus current | x | 8-DCMonitoring | getBus()
I_DC_MPPT_[1..X] |  | MPPT Current 1..X | x | 8-DCMonitoring | getMPTT()
P_DC |  | Total DC Power | x | 8-DCMonitoring | getBus()
P_DC_MPPT_[1..x] |  | DC Power MPPT 1…X | x | 8-DCMonitoring | getBus()
U_DC |  | DC Bus Voltage | x | 8-DCMonitoring | getBus()
U_DC_MPPT_[1..x] |  | MPPT Voltage 1..X | x | 8-DCMonitoring | getMPPT()
U_DC_STRING_[1..x] |  | String Voltage 1..X |  | 8-DCMonitoring | getString()
U_DC_NE |  | Negative Voltage to earth |  | 8-DCMonitoring | getBus()
U_DC_PE |  | Positive voltage to earth |  | 8-DCMonitoring | getBus()
I_DC_STRING_[1..X] |  | PV STRING Current 1..X |  | 8-DCMonitoring | getString()
R_ISO |  | Insulation Resistance | x
CMD_PF_ENA | OutPFSet_Ena
CMD_PF_RAMP_TIME_S | OutPFSet_RmpTms
CMD_PF_REVERT_TIME_S | OutPFSet_RvrtTms
UNIT_ID | SlaveAddress
CMD_COMMIT | Commit

## TAG_METER
Tags | Previous Tags | Description | MVP | Feature | Function
Monitoring
U_AC_L1L2 - L2L3 - L3L1 |  | AC Phase to phase Voltage 1..3 | x
U_AC_[1..3] |  | AC Phase to neutral Voltage 1..3
U_LE_AC_[1..3] |  | AC Phase to earth Voltage 1..3
U_NE |  | AC Neutral to Eearh
I_AC_[1..3] |  | AC Current Phase 1..3 | x
P_AC_[1..3] | ActivePow1..2..3kW | Active Power Phase 1..3 | x | ActivePowerMeasure | getActivePower()
P_AC | ActivePowSumkW | Total Active Power | x | ActivePowerMeasure | getActivePower()
Q_AC_[1..3] | ReactivePow1..2..3kW | Reactive Power Phase 1..3 | x
Q_AC | ReactivePowSumkW | total Reactive Power | x
S_AC_[1..3] |  | Apparent Power Phase 1..3 | x
S_AC |  | Total Apparent Power | x
PF_[1..3] |  | Power Factor Phase 1..3 | x
PF |  | Total Power Factor | x
FREQ_[1..3] |  | Frequency Phase 1..3 | x
FREQ |  | Total Frequency | x
E_TOT_[1..3] |  | Energy phase 1..3 | x
E_TOT |  | Total Energy | x
E_EXP_[1..3] |  | Export Energy Phase 1..3
E_EXP |  | Total Export Energy
E_IMP_[1..3] |  | Import Energy Phase 1..3
E_IMP |  | Total Import Energy
ES_[1..3] |  | Apparent Energy Phase 1..3
ES |  | Total Apparent Energy
ES_EXP_[1..3] |  | TotalExport Apparent Energy Phase 1..3
ES_EXP |  | TotalExport Apparent Energy
ES_IMP_[1..3] |  | TotalImport Apparent Energy Phase 1..3
ES_IMP |  | TotalImport Apparent Energy
EQ_[1..3] |  | Reactive Energy phase 1..3
EQ |  | Total Reactive Energy
EQ_EXP_[1..3] |  | TotalExport Reactive Energy phase 1..3
EQ_EXP |  | TotalExport Reactive Energy
EQ_IMP_[1..3] |  | Total Import Reactive Energy phase 1..3
EQ_IMP |  | Total Import Reactive Energy
SERIAL | DisplaySerial / DisplaySerialNumber | Serial Number of the meter
MODEL | DisplayModel | Model of the meter

## TAG_BATTERY
SOC
SOH
TEMP
U_DC

## TAG_SENSOR
Tags | Previous Tags | Description | MVP | Feature | Function | Column1
POA |  |  | x
GHI |  |  | x
TEMP_AMB |  |  | x
TEMP_CELL |  |  | x
SERIAL | DisplaySerial / DisplaySerialNumber
MODEL | DisplayModel
MANUFACTURER | ManufacturerStr

## TAG_DISPLAY
Tags | Previous Tags | Description | MVP | Feature | Function | Column1
P_AC | Pac-Tag
E_TOT | Eac-Tag
E_DAY | EacDay-Tag
AVOIDED_CO2 | Carb-Tag
AVOIDED_CO2_DAY | CarbDay-Tag
P_RATED
SELF_CONSUMPTION_RATIO | AutoConso-Tag
LOAD_P_AC | Conso-Tag
SERIAL | DisplaySerial
MODEL | DisplayModel
MANUFACTURER | ManufacturerStr

## TAG LOGGER
Tags | Previous Tags | Description | MVP | Feature | Function | Column1
CMD_OFF | cmdOff
CMD_ON | cmdOn
CMD_P_AC_SET_PERCENT | cmdPwrPercent
PF | CosPhi
E_DAY | EnergyDay
E_TOT | EnergyTotal
P_AC | RealPower

## TAG_PLANT
Tags | Description | Previous Tags | MVP | Feature | Function
E_DAY | Today Generation |  |  | plant | getInfo()
E_TOT | Total Génération |  |  | plant | getInfo()
CO2 | CO2 Avoided |  |  | plant | getInfo()
P_RATED | Plant Capacity |  |  | plant | getInfo()
P_AC | PV Active power |  |  | plant | getInfo()
P_EXPORTED | Exported power |  |  | plant | getInfo()
P_SELF | Self consumption |  |  | plant | getInfo()
TEMP_AMP | Ambient temperature |  |  | plant | getInfo()
TEMP_MODULE | Module temperature |  |  | plant | getInfo()
IRRADIANCE | Irradiance |  |  | plant | getInfo()
WIND_SPEED | Wind speed |  |  | plant | getInfo()
STATUS_PLANT | Plant status |  |  | plant | getInfo()
STATUS_INVERTERS | Inverters status |  |  | plant | getInfo()
PF | Power factor |  |  | plant | getInfo()

## TagsPrésents_18_12_25
Inverter | Meter | Display | Sensor
cmdAngle | ActivePow1kW | Eac-Tag | DeviceAddr
cmdOff | ActivePow2kW | Pac-Tag | DisplayModel
cmdOn | ActivePow3kW |  | DisplaySerialNumber
cmdPowerPercent | ActivePowSumkW
Commit | DisplayModel
ControlStation | DisplaySerialNumber
CosPhi
CtrlPwr_Ena
DailyEnergy
DisplayModel
DisplaySerialNumber
EnergyDay
EnergyTotal
GridFrequency
GridFrequency1
GridFrequency2
GridFrequency3
ManufacturerStr
NominalPower
Power Factor
QCtrlMode
QFPF_SP
QFQ_SP_kVar
Reactive Power
RealPower
signSinPhi
SlaveAddress
SmaIdFixedValue461
TotalEnergy
WattHours
Watts
WMaxLim_Ena
WMaxLimEna

## InverterBasicControl
BasicControl
Tags
CMD_ON | Write 1 to Start inverter
CMD_OFF | Write 1 to Stop inverter
Inverter Functions
hasInverterActiveControl()
True if at least one tag exists
inverterSetPowerOn(bool state)
state = true
Write 0 to CMD_ON
Write 1 to CMD_OFF
state = false
Write 0 to CMD_ON
Write 1 to CMD_OFF
Plant Functions
hasSolarActiveControl()
True if all solar inverters are compatibles
solarSetPowerOn(bool state)
for each solarInverter inverterSetPowerOn(bool state)

## InverterActiveControl
Tags
CMD_P_AC_LIM_PERCENT | Active Power Limitation in percent
CMD_P_AC_LIM_ABS | Active Power Limitation in kW
CMD_P_AC_SET_PERCENT | Active Power Setpoint in percent
CMD_P_AC_SET_ABS | Active Power Setpoint in kW
CMD_P_ENA | Power Limitation Enable Latch
CMD_RAMP_TIME_S | Ramp time for moving from current setpoint to new setpoint.
CMD_REVERT_TIME_S | Timeout period for power limit.
VAR_P_AC_REPEAT_TIME_S | Repeating time for P_AC control (Used as a constant)
P_RATED
Inverters Functions
inverterHasActiveControl
True if CMD_P_AC_SET_PERCENT or CMD_P_AC_SET_ABS
inverterSetRatedPowerKW(inverter, ratedPower)
Record rated power
inverterGetRatedPowerKW(inverter)
return value rated power (value set or, if none P_RATED, if none (Node Rated Power) / NbINVERTER in the node
inverterSetActivePowerPercent(inverter, percent)
if cmd_P_AC_setpct exists => Write value
if inverterGetRatedPowerKW = 0 : error
if cmd_P_AC_setabs : write (inverter_percent * ratedPower)
inverterSetActivePowerKW(inverter, power)
if cmd_P_AC_setabs : write (power)
if inverterGetRatedPowerKW = 0 : error
if cmd_P_AC_setpct exists => Write power/ratedPower
inverterSetACRampPercentPerSec(inverter, rampValue)
if (cmd_RmpTms) write value
inverterSetACRevertTimeSec(inverter, repeatValue)
if (cmd_RvrtTms) write value
BackgroundTask |  | In plant manager 5.3
var_P_AC_repeat : send last cmd_P_AC_setabs or cmd_P_AC_setpercent command
ConnectionEvent
If set : inverterSetACRampPercentPerSec(inverter, rampValue)
if set : inverterSetACRevertTimeSec(inverter, repeatValue)
SolarNode Functions
hasSolarActiveControl()
If each solarInverter has active control : return true
solarSetRatedPowerKW()
Set node rated power
solarGetRatedPowerKW()
return solarSetRatedPowerKW if any, else inverterGetRatedPowerKW for each inverter
solarSetActivePowerPercent(power)
For each inverter : setPowerPercent
solarSeActivetPowerKW(power)
Compute the % value then for each inverter setCommandPercent
solarSetACRampPercentPerSec(rampValue)
For each inverter in solar inverterSetACRampPercentPerSec(inverter, rampValue)
solarSetACRevertTimeSec(repeatValue)
for each inverter in solar : inverterSetACRevertTimeSec(inverter, repeatValue)
solarWriteActivePowerSettings()
Trigger a "connection event on each inverter"

## GridActivePower
Tags
M_P_AC_[1..3] | Active Power Phase 1..3
M_P_AC | Total Active Power
MeterFunctions
meterHasActivePower
True if at least one tag
meterGetActivePower(meter, min3phase)
Return age, Sum of 3 phase OR , if min3Phase the lowest phase *3
GridFunctions
gridHasActivePower
True if all grid meters has activePower
gridGetActivePower(min3phase)
Return the sum of meterGridActivePower for each meter in grid